## Table comparison
Proposal to EPTC based on EPC final curves
Table 1: Start-up types | Shutdown Period (hours) | Time from light-off to synchronise (minutes) | Time from Synchronise to Full Load (minutes) | Total time (minutes) | Table 2: Hot Start-up |  |  | Table 3: Warm Start-up |  |  | Table 4: Cold Start-up |  |  | Table 5: Initial Cold Start-up |  |  | Table 6: Ramp up in normal operation |  | Table 7: Ramp down in normal operation |  | Table 8: Shutdown |  | Table 9: Energy LD not apply in below cases: 1. Startup 2. Load change 3. Grid operates outside limit 4. Emergency 5. Force Majeure Event
Hot Start-up | Less than 8 | 75 | 145 | 220 | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Load | MW/min | Load | MW/min | Rate (MW/min): | 6.6
Warm Start-up | From 8 to 56 | 190 | 225 | 415 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 40% to 50% | 6.6 | 100% to 65% | 13.2 | Time from 40% load to 0% load (mins) | Net MW
Cold Start-up | From 56 to 72 | 310 | 280 | 590 | 4.8883 | 0 | 36 | 9.7765 | 0 | 36 | 9.7765 | 0 | 36 | 5.7207 | 0 | 21.48 | 50% to 65% | 13.2 | Hold 30 mins at 65% | 0 | 0 | 264
Initial Cold Start-up | More than 72 | 385 | 330 | 715 | 14.8603 | 71.4 | 107.4 | 13.7207 | 14.12 | 50.12 | 13.7207 | 14.12 | 50.12 | 65.7207 | 0 | 21.48 | Hold 30 mins at 65% | 0 | 65% to 50% | 13.2 | 40 | 264
[5 empty] | 54.8603 | 71.4 | 107.4 | 18.7207 | 14.12 | 50.12 | 23.7207 | 14.12 | 50.12 | 69.7765 | 0 | 36 | 65% to 100% | 13.2 | 50% to 40% | 6.6 | 50 | 198
[5 empty] | 81.7598 | 264 | 300 | 34.7207 | 71.4 | 107.4 | 39.7207 | 71.4 | 107.4 | 89.7207 | 71.4 | 107.4 |  |  |  |  | 105 | 198
[8 empty] | 74.7207 | 71.4 | 107.4 | 99.7207 | 71.4 | 107.4 | 149.7207 | 71.4 | 107.4 |  |  |  |  | 135 | 0
[8 empty] | 128.5196 | 264 | 300 | 153.5196 | 264 | 300 | 203.5196 | 264 | 300
[5 empty] | Table 2.1: Ramp rate from 40% to 100% after hot start-up |  |  | Table 3.1: Ramp rate from 40% to 100% after warm start-up |  |  | Table 4.1: Ramp rate from 40% to 100% after cold start-up |  |  | Table 5.1: Ramp rate from 40% to 100% after initial cold start-up
The first DI after reaching 40% will apply Start Up ramp rate in Table 2.1, Table 3.1, Table 4.1, Table 5.1 accordingly. And the other following DIs will apply normal operation ramp rate in Table 6 and Table 7 |  |  |  |  | Load | MW/min | Hold (mins) | Load | MW/min | Hold (mins) | Load | MW/min | Hold (mins) | Load | MW/min | Hold (mins)
[5 empty] | 40% to 50% | 6.6 |  | 40% to 50% | 3.3 |  | 40% to 50% | 3.3 |  | 40% to 50% | 3.3
[5 empty] | Hold 30 mins at 50% | 0 | 30 | Hold 30 mins at 50% | 0 | 30 | Hold 60 mins at 50% | 0 | 60 | Hold 60 mins at 50% | 0 | 60
[5 empty] | 50% to 100% | 13.2 |  | 50% to 100% | 6.6 |  | 50% to 100% | 6.6 |  | 50% to 100% | 6.6
[5 empty] | Table 2.2: Load Change from 40% to 100% after hot start-up |  |  | Table 3.2: Load Change from 40% to 100% after warm start-up |  |  | Table 4.2: Load Change from 40% to 100% after cold start-up |  |  | Table 5.2: Load Change from 40% to 100% after initial cold start-up
[5 empty] | Time (mins) | Net MW |  | Time (mins) | Net MW |  | Time (mins) | Net MW |  | Time (mins) | Net MW
[5 empty] | 0 | 264 |  | 0 | 264 |  | 0 | 264 |  | 0 | 264
[5 empty] | 10 | 330 |  | 20 | 330 |  | 20 | 330 |  | 20 | 330
[5 empty] | 40 | 330 |  | 50 | 330 |  | 80 | 330 |  | 80 | 330
[5 empty] | 65 | 660 |  | 100 | 660 |  | 130 | 660 |  | 130 | 660
From Predicted Curve in PPA
Table 1: Start-up types | Shutdown Period (hours) | Time from light-off to synchronise (minutes) | Time from Synchronise to Full Load (minutes) | Total time (minutes) | Table 2: Hot Start-up |  |  | Table 3: Warm Start-up |  |  | Table 4: Cold Start-up |  |  | Table 5: Initial Cold Start-up |  |  | Table 6: Ramp up in normal operation |  | Table 7: Ramp down in normal operation |  | Table 8: Shutdown |  | Table 9: Energy LD not apply in below cases: 1. Startup 2. Load change 3. Grid operates outside limit 4. Emergency 5. Force Majeure Event
Hot Start-up | Less than 8 | 75 | 145 | 220 | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Load | MW/min | Load | MW/min | Rate (MW/min): | 6.6
Warm Start-up | From 8 to 56 | 190 | 225 | 415 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 40% to 50% | 6.6 | 100% to 70% | 13.2 | Time from 40% load to 0% load (mins) | Net MW
Cold Start-up | From 56 to 72 | 310 | 280 | 590 | 4.8883 | 0 | 36 | 9.7765 | 0 | 36 | 9.7765 | 0 | 36 | 9.7765 | 0 | 36 | Hold 30 mins at 50% | 0 | Hold 30 mins at 70% | 0 | 0 | 264
Initial Cold Start-up | More than 72 | 385 | 330 | 715 | 14.8603 | 71.4 | 107.4 | 13.7207 | 14.12 | 50.12 | 13.7207 | 14.12 | 50.12 | 13.7207 | 14.12 | 50.12 | 50% to 100% | 13.2 | 70% to 40% | 13.2 | 40 | 264
[5 empty] | 54.8603 | 71.4 | 107.4 | 18.7207 | 14.12 | 50.12 | 23.7207 | 14.12 | 50.12 | 73.7207 | 14.12 | 50.12 |  |  |  |  | 50 | 198
[5 empty] | 81.7603 | 264.004 | 300.004 | 34.7207 | 71.4 | 107.4 | 39.7207 | 71.4 | 107.4 | 89.7207 | 71.4 | 107.4 |  |  |  |  | 105 | 198
[8 empty] | 74.7207 | 71.4 | 107.4 | 99.7207 | 71.4 | 107.4 | 149.7207 | 71.4 | 107.4 |  |  |  |  | 135 | 0
[8 empty] | 128.5207 | 264.004 | 300.004 | 153.5207 | 264.004 | 300.004 | 203.5207 | 264.004 | 300.004
[5 empty] | Table 2.1: Ramp rate from 40% to 100% after hot start-up |  |  | Table 3.1: Ramp rate from 40% to 100% after warm start-up |  |  | Table 4.1: Ramp rate from 40% to 100% after cold start-up |  |  | Table 5.1: Ramp rate from 40% to 100% after initial cold start-up
[5 empty] | Load | MW/min | Hold (mins) | Load | MW/min | Hold (mins) | Load | MW/min | Hold (mins) | Load | MW/min | Hold (mins)
|  |  | 1% |  | 40% to 50% | 6.6 |  | 40% to 50% | 3.3 |  | 40% to 50% | 3.3 |  | 40% to 50% | 3.3
|  |  | 6.6 |  | Hold 30 mins at 50% | 0 | 30 | Hold 30 mins at 50% | 0 | 30 | Hold 60 mins at 50% | 0 | 60 | Hold 60 mins at 50% | 0 | 60
[5 empty] | 50% to 100% | 13.2 |  | 50% to 100% | 6.6 |  | 50% to 100% | 6.6 |  | 50% to 100% | 6.6
[5 empty] | Table 2.2: Load Change from 40% to 100% after hot start-up |  |  | Table 3.2: Load Change from 40% to 100% after warm start-up |  |  | Table 4.2: Load Change from 40% to 100% after cold start-up |  |  | Table 5.2: Load Change from 40% to 100% after initial cold start-up
[5 empty] | Time (mins) | Net MW |  | Time (mins) | Net MW |  | Time (mins) | Net MW |  | Time (mins) | Net MW
[5 empty] | 0 | 264 |  | 0 | 264 |  | 0 | 264 |  | 0 | 264
[5 empty] | 10 | 330 |  | 20 | 330 |  | 20 | 330 |  | 20 | 330
[5 empty] | 40 | 330 |  | 50 | 330 |  | 80 | 330 |  | 80 | 330
[5 empty] | 65 | 660 |  | 100 | 660 |  | 130 | 660 |  | 130 | 660
Comparation

## Sheet1
G15701.2025.5591 | Vân Phong 1 | S2 | Khởi động lò |  |  | 2025-08-13 11:01 | 2025-08-13 11:01 | Table 1: Start-up types | Shutdown Period (hours) | Time from light-off to synchronise (minutes) | Time from Synchronise to Full Load (minutes) | Total time (minutes)
G15701.2025.5592 | Vân Phong 1 | S2 | Hoà lưới | 50 | 50 | 2025-08-13 12:52 | 2025-08-13 12:53 | Hot Start-up | Less than 8 | 75 | 145 | 220
G15701.2025.5593 | Vân Phong 1 | S2 | Thay đổi công suất | 264 | 264 | 2025-08-13 13:32 | 2025-08-13 14:58 | Warm Start-up | From 8 to 56 | 190 | 225 | 415
G15701.2025.5599 | Vân Phong 1 | S2 | Thay đổi công suất | 420.4 | 340 | 2025-08-13 15:10 | 2025-08-13 15:34 | Cold Start-up | From 56 to 72 | 310 | 280 | 590
G15701.2025.5603 | Vân Phong 1 | S2 | Thay đổi công suất | 660 | 660 | 2025-08-13 15:34 | 2025-08-13 16:35 | Initial Cold Start-up | More than 72 | 385 | 330 | 715
G15701.2025.5605 | Vân Phong 1 | S2 | Thay đổi công suất | 533.9 | 533.9 | 2025-08-14 00:02 | 2025-08-14 00:14
G15701.2025.5607 | Vân Phong 1 | S2 | Thay đổi công suất | 604 | 604 | 2025-08-14 00:41 | 2025-08-14 00:47 | Table 3: Warm Start-up
G15701.2025.5609 | Vân Phong 1 | S2 | Thay đổi công suất | 660 | 660 | 2025-08-14 01:01 | 2025-08-14 01:06 | Time from Syn to 40% load (mins) | Net MW | Gross MW
G15701.2025.5611 | Vân Phong 1 | S2 | Thay đổi công suất | 467.1 | 467.1 | 2025-08-14 01:56 | 2025-08-14 02:11 | 0 | 0 | 1
[8 empty] | 9.7765 | 0 | 36
[8 empty] | 13.7207 | 14.12 | 50.12
[8 empty] | 18.7207 | 14.12 | 50.12
| 2025-08-13 11:01 | Warm st | 0 |  |  |  |  | 34.7207 | 71.4 | 107.4
| 2025-08-13 14:11 | Syn_PPA | 0 |  |  |  |  | 74.7207 | 71.4 | 107.4
| 2025-08-13 14:21 |  | 0 |  |  |  |  | 128.5207 | 264.004 | 300.004
| 2025-08-13 14:25 |  | 14.12
| 2025-08-13 14:30 |  | 14.12 |  |  |  |  | Table 3.1: Ramp rate from 40% to 100% after warm start-up
| 2025-08-13 14:46 |  | 71.4 |  |  |  |  | Load | MW/min | Hold (mins)
| 2025-08-13 14:58 | Completed minload | 264 |  |  |  |  | 40% to 50% | 3.3
| 2025-08-13 15:10 | Load change after start-up | 264 |  |  |  |  | Hold 30 mins at 50% | 0 | 30
| 2025-08-13 15:30 |  | 330 |  |  |  |  | 50% to 100% | 6.6
| 2025-08-13 16:00 |  | 330
| 2025-08-13 16:01 |  | 340

## Curve comparison
Table 2: Hot Start-up |  |  | Table 3: Warm Start-up |  |  | Table 4: Cold Start-up |  |  | Table 5: Initial Cold Start-up
Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW
0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
4.8883 | 0 | 36 | 9.7765 | 0 | 36 | 9.7765 | 0 | 36 | 5.7207 | 0 | 21.48
14.8603 | 71.4 | 107.4 | 13.7207 | 14.12 | 50.12 | 13.7207 | 14.12 | 50.12 | 65.7207 | 0 | 21.48
54.8603 | 71.4 | 107.4 | 18.7207 | 14.12 | 50.12 | 23.7207 | 14.12 | 50.12 | 69.7765 | 0 | 36
81.7603 | 264.004 | 300.004 | 34.7207 | 71.4 | 107.4 | 39.7207 | 71.4 | 107.4 | 89.7207 | 71.4 | 107.4
91.7603 | 330 |  | 74.7207 | 71.4 | 107.4 | 99.7207 | 71.4 | 107.4 | 149.7207 | 71.4 | 107.4
121.7603 | 330 |  | 128.5207 | 264.004 | 300.004 | 153.5207 | 264.004 | 300.004 | 203.5207 | 264.004 | 300.004
146.7603 | 660 |  | 148.5207 | 330 |  | 173.5207 | 330 |  | 223.5207 | 330
|  |  | 178.5207 | 330 |  | 233.5207 | 330 |  | 283.5207 | 330
|  |  | 228.5207 | 660 |  | 283.5207 | 660 |  | 333.5207 | 660
Table 2: Hot Start-up |  |  | Table 3: Warm Start-up |  |  | Table 4: Cold Start-up |  |  | Table 5: Initial Cold Start-up
Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW | Time from Syn to 40% load (mins) | Net MW | Gross MW
0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
4.8883 | 0 | 36 | 9.7765 | 0 | 36 | 9.7765 | 0 | 36 | 9.7765 | 0 | 36
14.8603 | 71.4 | 107.4 | 13.7207 | 14.12 | 50.12 | 13.7207 | 14.12 | 50.12 | 13.7207 | 14.12 | 50.12
54.8603 | 71.4 | 107.4 | 18.7207 | 14.12 | 50.12 | 23.7207 | 14.12 | 50.12 | 73.7207 | 14.12 | 50.12
81.7603 | 264.004 | 300.004 | 34.7207 | 71.4 | 107.4 | 39.7207 | 71.4 | 107.4 | 89.7207 | 71.4 | 107.4
91.7603 | 330 |  | 74.7207 | 71.4 | 107.4 | 99.7207 | 71.4 | 107.4 | 149.7207 | 71.4 | 107.4
121.7603 | 330 |  | 128.5207 | 264.004 | 300.004 | 153.5207 | 264.004 | 300.004 | 203.5207 | 264.004 | 300.004
146.7603 | 660 |  | 148.5207 | 330 |  | 173.5207 | 330 |  | 223.5207 | 330
|  |  | 178.5207 | 330 |  | 233.5207 | 330 |  | 283.5207 | 330
|  |  | 228.5207 | 660 |  | 283.5207 | 660 |  | 333.5207 | 660
Time in normal operation (proposal) | Load
0 | 264.004
9.9994 | 330
17.4994 | 429
47.4994 | 429
64.9994 | 660
94.9994 | 660
112.4994 | 429
142.4994 | 429
149.9994 | 330
159.9988 | 264.004
Time in normal operation (PPA) | Load
0 | 264.004
9.9994 | 330
39.9994 | 330
64.9994 | 660
94.9994 | 660
109.9994 | 462
139.9994 | 462
154.9991 | 264.004

## LD comparison
Monthly Liquidated Damages (8.1b of PPA)
Unit: VND
|  |  |  | 2023-10-01 | 2023-11-01 | 2023-12-01 | 2024-01-01 | 2024-02-01 | 2024-03-01 | 2024-04-01 | 2024-05-01 | 2024-06-01 | 2024-07-01 | 2024-08-01 | 2024-09-01 | 2024-10-01 | 2024-11-01 | 2024-12-01 |  | Total
| EPTC (PPA curve) | CLD | Unit 1 | 2023-10-01: 153222211; 2023-11-01: 169212496; 2023-12-01: 161873883; 2024-01-01: 217414168; 2024-02-01: 111808684; 2024-03-01: 63907001; 2024-04-01: 131689054; 2024-05-01: 191325409
|  |  | Unit 2 | 2024-01-01: 285080376; 2024-02-01: 202973702; 2024-03-01: 65802602; 2024-04-01: 163614767; 2024-05-01: 165447504
|  | ELD | Unit 1 | 2023-10-01: 0; 2023-11-01: 0; 2023-12-01: 1261936; 2024-01-01: 619331; 2024-02-01: 171004; 2024-03-01: 0
|  |  | Unit 2 | 2024-01-01: 0; 2024-02-01: 535570; 2024-03-01: 0
|  | Total | VND | 2023-10-01: 153222211; 2023-11-01: 169212496; 2023-12-01: 163135819; 2024-01-01: 503113875; 2024-02-01: 315488960; 2024-03-01: 129709603; 2024-04-01: 295303821; 2024-05-01: 356772913 | 0 | 2085959698
|  |  | USD | 2023-10-01: 6384.2588; 2023-11-01: 7050.5207; 2023-12-01: 6797.3258; 2024-01-01: 20963.0781; 2024-02-01: 13145.3733; 2024-03-01: 5404.5668; 2024-04-01: 12304.3259; 2024-05-01: 14865.538
| VPCL (EPC curve) | CLD | Unit 1 | 2023-10-01: 78639388; 2023-11-01: 153115471.3166; 2023-12-01: 149807175.1586; 2024-01-01: 110007210; 2024-02-01: 3979660.6736; 2024-03-01: 1538944; 2024-04-01: 26467306.4214; 2024-05-01: 39948418
|  |  | Unit 2 | 2024-01-01: 235074185; 2024-02-01: 76269725.2857; 2024-03-01: 18519298; 2024-04-01: 0; 2024-05-01: 56753891
|  | ELD | Unit 1 | 2023-10-01: 0; 2023-11-01: 0; 2023-12-01: 1460959.356; 2024-01-01: 0
|  |  | Unit 2 | 2024-01-01: 0
|  | Total | VND | 2023-10-01: 78639388; 2023-11-01: 153115471.3166; 2023-12-01: 151268134.5146; 2024-01-01: 345081395; 2024-02-01: 80249385.9593; 2024-03-01: 20058242; 2024-04-01: 26467306.4214; 2024-05-01: 96702309 | 0 | 951581632.2119
|  |  | USD | 2023-10-01: 3276.6412; 2023-11-01: 6379.8113; 2023-12-01: 6302.8389; 2024-01-01: 14378.3915; 2024-02-01: 3343.7244; 2024-03-01: 835.7601; 2024-04-01: 1102.8044; 2024-05-01: 4029.2629
|  | Diff | VND | 2023-10-01: 74582823; 2023-11-01: 16097024.6834; 2023-12-01: 11867684.4854; 2024-01-01: 158032480; 2024-02-01: 235239574.0407; 2024-03-01: 109651361; 2024-04-01: 268836514.5786; 2024-05-01: 260070604 | 0 | 1134378065.7881
|  |  | USD | 2023-10-01: 3107.6176; 2023-11-01: 670.7094; 2023-12-01: 494.4869; 2024-01-01: 6584.6867; 2024-02-01: 9801.6489; 2024-03-01: 4568.8067; 2024-04-01: 11201.5214; 2024-05-01: 10836.2752
|  |  |  | In NIA Nov. 23 | In NIA Dec. 23 | In NIA Jan. 24 | In NIA Feb. 24
Monthly LD
Billing month: |  | 2023-10-31 | bar: 2023-10-01 to 2023-11-01
|  | 2023-11-07 |  | 2023-10-01: Issue NIA of Oct-2023; 2023-11-01: M1
| 20 | 2023-11-20 |  | 2023-10-01: EPTC send LD's amount of Oct-2023
| 15 | 2023-12-05 |  | 2023-10-01: VPCL's feedback of disputed amount of Oct-2023; 2023-11-01: M2
Billing month: |  | 2023-11-30 | bar: 2023-10-01
|  | 2023-12-07 |  | 2023-10-01: Issue NIA of Nov-2023 and undisputed amount of LD Oct. 2023
|  | 2023-12-11 |  | 2023-10-01: Issue VAT invoice of Oct-2023
|  | 2023-12-12 |  | 2023-10-01: EVN make payment of NIA - Oct. 2023
|  | 2023-12-20 |  | 2023-10-01: EPTC send LD's amount of Nov. 2023
|  | 2024-01-04 |  | 2023-10-01: VPCL's feedback of disputed amount of Nov-2023; 2023-11-01: M3
Billing month: |  | 2023-12-31 | bar: 2023-10-01
|  | 2024-01-07 |  | 2023-10-01: Issue NIA of Dec-2023 and undisputed amount of LD Nov. 2023
|  | 2024-01-11 |  | 2023-10-01: Issue VAT invoice of Nov-2023 deducting undisputed amount of LD Oct. 23
|  | 2024-01-12 |  | 2023-10-01: EVN make payment Tariff Nov. 2023
|  | 2024-01-20 |  | 2023-10-01: EPTC send LD's amount of Dec. 2023
|  | 2024-02-04 |  | 2023-10-01: VPCL's feedback of disputed amount of Dec-2023
Billing month: |  | 2024-01-31 | bar: 2023-10-01
|  | 2024-02-07 |  | 2023-10-01: Issue NIA of Jan-2024 and undisputed amount of LD Dec. 2023
|  | 2024-02-11 |  | 2023-10-01: Issue VAT invoice of Dec-2023 deducting undisputed amount of LD Nov. 23
|  | 2024-02-12 |  | 2023-10-01: EVN make payment Tariff Dec. 2023
|  | 2024-02-20 |  | 2023-10-01: EPTC send LD's amount of Jan. 2024
|  | 2024-03-06 |  | 2023-10-01: VPCL's feedback of disputed amount of Jan. 2024
Billing month: |  | 2024-02-29 | bar: 2023-10-01
|  | 2024-03-07 |  | 2023-10-01: Issue NIA of Feb-2024 and undisputed amount of LD Jan. 2024
|  | 2024-03-11 |  | 2023-10-01: Issue VAT invoice of Jan-2024 deducting undisputed amount of LD Dec. 23
|  | 2024-03-12 |  | 2023-10-01: EVN make payment Tariff Jan. 2024
|  | 2024-03-20 |  | 2023-10-01: EPTC send LD's amount of Feb. 2024
|  | 2024-04-04 |  | 2023-10-01: VPCL's feedback of disputed amount of Feb. 2024
Billing month: |  | 2024-03-31 | bar: 2023-10-01
|  | 2024-04-07 |  | 2023-10-01: Issue NIA of Mar-2024 and undisputed amount of LD Feb. 2024
|  | 2024-04-11 |  | 2023-10-01: Issue VAT invoice of Feb-2024 deducting undisputed amount of LD Jan. 24
|  | 2024-04-12 |  | 2023-10-01: EVN make payment Tariff Feb. 2024
|  | 2024-04-20 |  | 2023-10-01: EPTC send LD's amount of Mar. 2023
|  | 2024-05-05 |  | 2023-10-01: VPCL's feedback of disputed amount of Mar. 2024
Billing month: |  | 2024-04-30 | bar: 2023-10-01
|  | 2024-05-07 |  | 2023-10-01: Issue NIA of Mar-2024 and undisputed amount of LD Feb. 2024
|  | 2024-05-11 |  | 2023-10-01: Issue VAT invoice of Feb-2024 deducting undisputed amount of LD Jan. 24
|  | 2024-05-12 |  | 2023-10-01: EVN make payment Tariff Feb. 2024
|  | 2024-05-20 |  | 2023-10-01: EPTC send LD's amount of Mar. 2023
|  | 2024-06-04 |  | 2023-10-01: VPCL's feedback of disputed amount of Mar. 2024

## Advance Notice
Start-up with 1 unit online | Advance Notice (hrs) | Start-up Aux Boiler/Line up Aux Steam (hrs) | Condenser Hotwell Filling (hrs) | Condensate system start (hrs) | LP CU Blow/Cir (hrs) | Feedwater Start (hrs) | HP CU blow/Cir (hrs) | Boiler filling (hrs) | Boiler cold CU blow/Cir (hrs) | Boiler hot CU blow/Cir (hrs) | Start-up mode | Hrs
Hot Start-up | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hot Start-up | < 8
Warm Start-up | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Warm Start-up | >=8 to 56
Cold Start-up | 22 | 0 | 3 | 3 | 3 | 1 | 3 | 2 | 4 | 3 | Cold Start-up | >= 56 to 72
Innitial Cold | 22 | 0 | 3 | 3 | 3 | 1 | 3 | 2 | 4 | 3 | Innitial Cold | >=72
Start-up with both unit offline | Advance Notice (hrs) | Start-up Aux Boiler/Line up Aux Steam (hrs) | Condenser Hotwell Filling (hrs) | Condensate system start (hrs) | LP CU Blow/Cir (hrs) | Feedwater Start (hrs) | HP CU blow/Cir (hrs) | Boiler filling (hrs) | Boiler cold CU blow/Cir (hrs) | Boiler hot CU blow/Cir (hrs) | Put Unit in Presevation | After unit shutdown (hrs)
Hot Start-up | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Increase pH water | 56
Warm Start-up | 5 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Fill N2 Boiler and Heater | 72
Cold Start-up | 26 | 4 | 3 | 3 | 3 | 1 | 3 | 2 | 4 | 3
Innitial Cold | 26 | 4 | 3 | 3 | 3 | 1 | 3 | 2 | 4 | 3 | Start-up Auxboiler | Hrs
[11 empty] | Drain high Ph water | 0.5
[11 empty] | Fill Demin water | 0.5
[11 empty] | Flushing | 1
[11 empty] | Boiler firing to reach 20kg/cm2 | 2
[11 empty] | Sum | 4